## Chemical Consumption
Chemical consumption
Sr.No | Chemical | Concentration of Chemical in % | Tank capacity in Liter | Dosing pump capacity in LPH | Dosing PPM | Line Feed flow in m3/Hr | Concentration in tank | Qty/hr required in kg | Operating hrs | Qty/day required in kg | Qty per month considering 24 hr operation | Remarks
1 | FeCL3 (Coagulant) | 40 | 250 | 15 | 25 | 122 | 10 | 7.625 | 24 | 183 | 5490
2 | polyelectrolyte | 100 | 600 | 30 | 1 | 122 | 0.5 | 0.122 | 24 | 2.928 | 87.84
3 | HCL | 33 | 350 | 5 | 60 | 120 | 33 | 21.8182 | 24 | 523.6364 | 15709.0909
4 | Antiscalent | 100 | 150 | 10 | 5 | 120 | 10 | 0.6 | 24 | 14.4 | 432
5 | SMBS | 100 | 150 | 10 | 3 | 120 | 10 | 0.36 | 24 | 8.64 | 259.2
6 | Dolomatic Lime | 100 | 7000 | 500 | 230 | 122 | 10 | 28.06 | 24 | 673.44 | 20203.2