## Solids Retention Time
Directions: | [7 empty] | Date calculated:
Input numbers - yellow boxes
Output calculation - green boxes
SRT - orange box
1. Size of aeration tank
Length | 60 | feet | Width | 175 | feet |  |  | Water Depth | 15 | feet | Volume | 1.1781 | MG
2. Size of Clarifier
Diameter |  | 85 | feet | Water Depth |  | 12 | feet | Volume | 0.50909 | MG
3. Total Volume of Aeration tank and Clarifier
| 1.6872 | MG
4. MLSS or MLVSS Concentration
| 3450 | mg/L
5. Waste Sludge Concentration
| 6230 | mg/L
6. Waste Sludge Flow
| 0.084 | MGD
7. Effluent TSS Concentration
| 15 | mg/L
8. Average Wastewater Flow |  |  |  | 9. Calculated SRT |  |  | 10.2883 | Days
| 2.83 | MGD
Solids Retention Time (SRT) Calculation Worksheet