## FeedWater
FEED WATER
Feed Water | pH | Conductivity | TDS | Total | Chloride | Total | Calcium | Magnesium | Iron | Arsenic | MoO₄
|  | µs/cm |  | Alkalinity |  | Hardness | Hardness | Hardness
Date |  |  | mg/l | mg/l as CaCO3 | mg/l Cl- | mg/l as CaCO3 | mg/l as CaCO3 | mg/l as CaCO3 | mg/l Fe | mg/L As | mg/l
OPERATION LIMITS
min | 6.5 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50
max | 8 | 100 | 50 | 100 | 10 | 10 | 5 | 5 | 0.1 | 0.01 | 150
2017-01-04 | 8.82 | 763 | 419 | 230 | 7 | 0 | 0 | 0 | 0 | 1.596 | 315.35
2017-01-05 | 8.81 | 798 | 439 | 140 | 6 | 1 | 1 | 0 | 0 | 1.589 | 304.3
2017-01-06 | 8.64 | 668 | 367 | 100 | 5 | 0 | 0 | 0 | 0 | 1.318 | 282.4
2017-01-09 | 7.86 | 589 | 324 | 70 | 4 | 1 | 1 | 0 | 0 | 1.108 | 259.3
2017-01-10 | 7.88 | 582 | 320 | 100 | 5 | 3 | 3 | 0 | 0 | 1.079 | 243
2017-01-11 | 7.92 | 587 | 323 | 150 | 3 | 3 | 3 | 0 | 0 | 1.164 | 250
2017-01-12 | 7.82 | 570 | 314 | 90 | 5 | 0 | 0 | 0 | 0 | 1.329 | 196
2017-01-13 | 7.54 | 556 | 306 | 70 | 6 | 0 | 0 | 0 | 0 | 1.308 | 202
2017-01-16 | 7.71 | 514 | 283 | 70 | 4 | 0 | 0 | 0 | 0 | 1.3 | 210.63
2017-01-17 | 7.22 | 403 | 222 | 40 | 5 | 0 | 0 | 0 | 0 | 0.975 | 166
2017-01-18 | 6.73 | 122 | 67 | 40 | 5 | 0 | 0 | 0 | 0 | 0.192 | 37
2017-01-19 | 6.83 | 191 | 105 | 50 | 5 | 0 | 0 | 0 | 0 | 0.529 | 91
2017-01-20 | 6.85 | 191 | 105 | 50 | 4 | 0 | 0 | 0 | 0 | 0.439 | 87
2017-01-23 | 7.05 | 190 | 105 | 40 | 5 | 0 | 0 | 0 | 0 | 0.436 | 88
2017-01-24 | 7.06 | 200 | 110 | 40 | 4 | 0 | 0 | 0 | 0 | 0.475 | 94
2017-01-25 | 7.08 | 184 | 101 | 60 | 4 | 0 | 0 | 0 | 0 | 0.411 | 84
2017-01-26 | 6.98 | 187 | 103 | 40 | 4 | 0 | 0 | 0 | 0 | 0.497 | 86
2017-01-27 | 6.97 | 182 | 100 | 50 | 2 | 0 | 0 | 0 | 0 | 0.485 | 82
2017-01-30 | 6.99 | 160 | 88 | 40 | 4 | 0 | 0 | 0 | 0 | 0.446 | 66
2017-01-31 | 6.68 | 140 | 77 | 20 | 2 | 0 | 0 | 0 | 0 | 0.661 | 49
2017-02-01 | 6.77 | 138 | 76 | 40 | 5
2017-02-02 | 6.67 | 147 | 81 | 40 | 5 | 0 | 0 | 0 | 0 | 0.715 | 57
2017-02-03 | 7.2 | 230 | 127 | 60 | 7 | 0 | 0 | 0 | 0 | 1.09 | 103.43
2017-02-06 | 7.45 | 272 | 150 | 70 | 5 | 0 | 0 | 0 | 0 | 0.68 | 105.89
2017-02-07 | 7.83 | 338 | 186 | 50 | 4 | 0 | 0 | 0 | 0 | 0.935 | 131
2017-02-08 | 7.44 | 467 | 257 | 60 | 4 | 0 | 0 | 0 | 0 | re-assay | 186
2017-02-09 | 6.29 | 63 | 35 | 40 | 2 | 25 | 6 | 19 | 0.119 | 0.273 | 2.23
2017-02-10 | 6.94 | 370 | 204 | 60 | 4 | 0 | 0 | 0 | 0 | 1.178 | 186.3
2017-02-13 | 7.1 | 374 | 206 | 70 | 4 | 0 | 0 | 0 | 0 | 1.284 | 210
2017-02-14 | 7.09 | 368 | 202 | 60 | 4 | 0 | 0 | 0 | 0 | 1.105 | 160
2017-02-15 | 7.23 | 375 | 206 | 80 | 4 | 2 | 2 | 0 | 0.017 | 0.848 | 150
2017-02-16 | 7.13 | 383 | 211 | 50 | 4 | 0 | 0 | 0 | 0 |  | 159
2017-02-17 | 7.15 | 403 | 222 | 40 | 4 | 0 | 0 | 0 | 0 | 1.751 | 134
2017-02-20 | 7 | 361 | 199 | 70 | 2 | 0 | 0 | 0 | 0 | 0.844 | 151
2017-02-21 | 7.01 | 372 | 205 | 60 | 5 | <1 | <1 | 0 | 0 | 0.941 | 128
2017-02-22 | 6.95 | 369 | 203 | 80 | 4 | 0 | 0 | 0 | 0 | 0.935 | 129
2017-02-23 | 6.99 | 368 | 202 | 70 | 5 | 0.558 | 0.558 | 0 | 0.006 | 1.291 | 135.51
2017-02-24 | 6.93 | 330 | 182 | 120 | 5 | 0 | 0 | 0 | 0 | 1.019 | 131.988
2017-02-27 | 6.17 | 63 | 35 | 20 | 4 | 0 | 0 | 0 | 0 | 0.047 | 6.8
2017-02-28 | 6.74 | 390 | 215 | 130 | 19 | 4 | 4 | 0 | 0 | 0.1 | 1.45
2017-03-01 | 6.55 | 300 | 165 | 80 | 16 | 11 | 8 | 3 | 0 | 0.23 | 0.34
2017-03-02 | 6.55 | 258 | 142 | 70 | 13 | 20 | 10 | 10 | 0.115 | 0.309 | 1
2017-03-03 | 7.62 | 582 | 320 | 130 | 2 | <1 | <1 | 0 | 0 | 0.916 | 188
2017-03-06 | 8.8 | 1136 | 625 | 180 | 6 | 2 | 2 | <1 | 0 | 2.074 | 377
2017-03-07 | 8.61 | 961 | 529 | 180 | 6 | 41 | 4 | 1 | 0 | 1.707 | 322
2017-03-08 | 7.02 | 310 | 171 | 70 | 5 | 4 | 1 | 3 | 0 | 0.113 | 43
2017-03-09 | 8.25 | 1114 | 613 | 200 | 5 | 32 | 15 | 17 | 0.236 | 1.91 | 356
2017-03-10 | 8.1 | 1126 | 619 | 230 | 16 | 4 | 3 | 1 | 0 | 1.836 | 369.24
2017-03-13 | 6.83 | 296 | 163 | 50 | 4 | 0 | 0 | 0 | 0 | 0.407 | 72
2017-03-14 | 6.65 | 123 | 68 | 50 | 5 | 0 | 0 | 0 | 0 | 0.047
2017-03-15 | 6.95 | 250 | 138 | 50 | 2 | 0 | 0 | 0
2017-03-16 | 6.99 | 273 | 150 | 80 | 4 | 4 | 4 | 0
2017-03-17 | 7 | 247 | 136 | 69 | 4 | 7 | 7 | 0
2017-03-20 | 6.55 | 81 | 45 | 40 | 4 | 0 | 0 | 0 | 0 | 0.002
2017-03-22 | No Sample
2017-03-23 | 6.92 | 144 | 79 | 50 | 4 | 26 | 8 | 18
2017-03-24 | 6.97 | 149 | 82 | 70 | 6 | 7 | 2 | 5
2017-03-27 | 6.95 | 167 | 92 | 90 | 2 | 3 | 2 | 1
2017-03-28 | 6.84 | 135 | 74 | 60 | 4 | 2 | 1 | 1
2017-03-29 | 7.03 | 142 | 78 | 50 | 4 | 4 | 1 | 3
2017-03-30 | 7.01 | 144 | 79 | 40 | 2 | 4 | 2 | 2
2017-03-31 | 6.82 | 120 | 66 | 50 | 4 | 6 | 2 | 4
2017-04-01 | 6.77 | 126 | 69 | 80 | 2 | 4 | 2 | 2
2017-04-04 | 7.12 | 144 | 79 | 80 | 4 | 3 | 1 | 2
2017-04-05 | 6.45 | 55 | 30 | 40 | 4 | 2 | 1 | 1
2017-04-06 | 6.53 | 75 | 41 | 50 | 2 | 3 | 1 | 2
2017-04-07 | 6.67 | 77 | 42 | 30 | 4 | 3 | 2 | 1
2017-04-10 | 6.73 | 82 | 45 | 50 | 2 | 4 | 2 | 2
2017-04-11 | 6.63 | 98 | 54 | 40 | 4 | 4 | 3 | 1
2017-04-12 | No Sample
2017-04-13 | 6.71 | 81 | 45 | 40 | 4 | 4 | 1 | 3
2017-04-18 | 6.86 | 89 | 49 | 50 | 2 | 4 | 2 | 2
2017-04-19 | 6.76 | 81 | 45 | 30 | 2 | 4 | 3 | 1
2017-04-20 | 7.02 | 80 | 44 | 30 | 4 | 4 | 3 | 1
2017-04-21 | 7.2 | 77 | 42 | 40 | 4 |  | 3
2017-04-24 | 6.77 | 66 | 36 | 40 | 2 |  | 3
2017-04-25 | 6.71 | 61 | 34 | 20 | 4 |  | 1
2017-04-26 | 6.71 | 64 | 35 | 40 | 4 |  | 3
2017-04-27 | 7.08 | 62 | 34 | 40 | 5 |  | 6
2017-04-28 | 6.8 | 75 | 41 | 40 | 4 |  | 2
2017-05-02 | 6.75 | 72 | 40 | 40 | 2 |  | 3
2017-05-03 | 6.67 | 72 | 40 | 40 | 4 |  | 2
2017-05-05 | 7.85 | 74 | 41 | 50 | 4 |  | 3
2017-05-08 | 6.6 | 45 | 25 | 40 | 4 |  | 2
2017-05-09 | 6.33 | 59 | 32 | 40 | 2 |  | 4
2017-05-10 | 6.41 | 55 | 30 | 30 | 7 |  | 3
2017-05-11 | 6.16 | 50 | 28 | 20 | 4 |  | 3
2017-05-12 | No Sample
2017-05-15 | 6.13 | 47 | 26 | 40 | 5 |  | 5
2017-05-16 | 6.28 | 47 | 26 | 40 | 2 |  | 3
2017-05-17 | 6.74 | 140 | 77 | 60 | 4 |  | 2
2017-05-18 | 9.33 | 289 | 159 | 110 | 4 |  | 3
2017-05-19 | 6.37 | 144 | 79 | 80 | 4 | 0 | 0 | 0 | 0 | 0.353 | 41
2017-05-22 | 8.19 | 158 | 87 | 70 | 4 | 0 | 0 | 0 | 0 | 0.384 | 46.4
2017-05-23 | 11.25 | 1349 | 742 | 240 | 5 | 1 | 1 | 0 | 0 | 15.53 | 380.3
2017-05-24 | 10.51 | 787 | 433 | 160 | 5 | 0 | 0 | 0 | 0 | 1.965 | 283
2017-05-26 | 10.23 | 440 | 242 | 150 | 4 | 0 | 0 | 0 | 0 | 0.164 | 164.3
2017-05-29 | 11.44 | 2240 | 1232 | 590 | 10 | 2 | 2 | 0 | 0.214 | 5.152 | 561
2017-05-30 | 11.39 | 1751 | 963 | 370 | 7 | 0 | 0 | 0 | 0.034 | 4.226 | 528.2
2017-05-31 | 11.52 | 2070 | 1139 | 630 | 5 | 0 | 0 | 0 | 0.1 | 5.233 | 580
2017-06-01 | 11.38 | 2240 | 1232 | 530 | 5 | 1 | 1 | 0 | 0.142 | 5.218 | 565
2017-06-02 | 11.41 | 1831 | 1007 | 640 | 16 | 0 | 0 | 0 | 0 | 4.43 | 543.3
2017-06-05 | 11.37 | 1791 | 985 | 60 | 12 | 0 | 0 | 0 | 0.118 | 5.47 | 550
2017-06-06 | 11.44 | 1757 | 966 | 1040 | 4 | 0 | 0 | 0 | 0.148 | 5.037 | 536
2017-06-07 | 11.38 | 1796 | 988 | 300 | 6 | 0.67 | 0.67 | 0 | 0.17 | 4.79 | 544
2017-06-08 | 11.36 | 1806 | 993 | 530 | 7 | 3 | 2 | 1 | 0.172 | 4.693 | 619
2017-06-09 | 11.15 | 1661 | 914 | 390 | 6 | 0 | 0 | 0 | 0.02 | 4.527 | 573.4
2017-06-12 | 11.36 | 1769 | 973 | 830 | 6 | 5 | 3 | 2 | 0.082 | 5.27 | 638
2017-06-13 | 11.23 | 1673 | 920 | 200 | 7 | 1 | 1 | 0 | 0.226 | 5.783 | 727
2017-06-14 | 11.5 | 1731 | 952 | 380 | 5 | 2 | 2 | 0.123 | 0.197 |  | 639
2017-06-15 | 11.39 | 1666 | 916 | 910 | 7 | 14 | 5 | 9 | 0.357 | 5.643 | 673
2017-06-16 | 11.49 | 1325 | 728 | 300 | 8 | 8 | 3 | 5 | 0.243 | 4.372 | 541
2017-06-19 | 11.25 | 1549 | 852 | 410 | 6 | 2 | 2 | 0 | 0.16 | 3.99 | 529
2017-06-20 | 10.83 | 849 | 467 | 530 | 5 | 0 | 0 | 0 | 0 | 2.295 | 318
2017-06-21 | 10.37 | 1048 | 576 | 260 | 5 | 0 | 0 | 0 | 0 | 3.212 | 368
2017-06-22 | 10.38 | 1054 | 580 | 450 | 5 | 0 | 0 | 0 | 0 | 2.646 | 351
2017-06-23 | 9.07 | 962 | 529 | 390 | 4 | 2 | 0 | 2 | 0.246 | 4.065 | 240
2017-06-26 | 9.14 | 986 | 542 | 140 | 5 | 28 | 13 | 15 | 0.48 | 1.218 | 415
2017-06-27 | 9.15 | 965 | 964 | 380 | 4 | 0 | 0 | 0 | 0 | 1.869 | 226.3
2017-06-28 | 9.13 | 903 | 497 | 340 | 5 | 4 | 2 | 2 | 0.077 | 2.164 | 389
2017-06-29 | 9.11 | 877 | 482 | 240 | 5 | 0 | 0 | 0 | 0 | 2.296 | 355
2017-06-30 | 9.96 | 926 | 510 | 420 | 5 | 1 | 1 | 0 | 0 | 2.51 | 376
2017-07-03 | 9.37 | 808 | 444 | 150 | 4 | 0 | 0 | 0 | 0 | 2.752 | 358
2017-07-04 | 7.48 | 378 | 208 | 120 | 4 | 0 | 0 | 0 | 0 | 1.068 | 171
2017-07-05 | 7.41 | 411 | 226 | 130 | 5 | 0 | 0 | 0 | 0 | 1.052 | 175
2017-07-06 | 7.42 | 410 | 226 | 110 | 5 | 0 | 0 | 0 | 0 | 1.298 | 175
2017-07-07 | 7.4 | 409 | 225 | 190 | 4 | 0 | 0 | 0 | 0 | 1.79 | 159
2017-07-10 | 7.78 | 383 | 211 | 130 | 5 | 0 | 0 | 0 | 0 | 0.81 | 161
2017-07-11 | 9.27 | 407 | 224 | 130 | 4 | 0 | 0 | 0 | 0 | 0.913 | 9
2017-07-12 | 7.9 | 387 | 213 | 90 | 5 | 0 | 0 | 0 | 0 | 0.913 | 142
2017-07-13 | 8.16 | 418 | 230 | 130 | 6 | 0 | 0 | 0 | 0 | 1.004 | 164
2017-07-14 | 8.2 | 422 | 232 | 110 | 5 | 0 | 0 | 0 | 0 | 1.009 | 164
2017-07-17 | 8.05 | 418 | 230 | 150 | 6 | 4 | 3 | 1 | 0.056 | 1.016 | 160
2017-07-18 | 7.1 | 412 | 227 | 170 | 4 | 0 | 0 | 0 | 0 | 1.137 | 182
2017-07-19 | 7.61 | 348 | 191 | 80 | 4 | 0 | 0 | 0 | 0 | 0.989 | 141
2017-07-20 | 6.43 | 320 | 176 | 100 | 5 | 0 | 0 | 0 | 0 | 0.642 | 118
2017-07-21 | 6.93 | 367 | 202 | 110 | 0 | 0 | 0 | 0 | 0 | 1.056 | 135
2017-07-24 | 6.64 | 376 | 207 | 80 | 4 | 0 | 0 | 0 | 0 | 0.871
2017-07-25 | 7.31 | 410 | 226 | 80 | 4 | 0 | 0 | 0 | 0 | 8.205 | 136.4
2017-07-26 | 7.21 | 319 | 175 | 60 | 4 | 0 | 0 | 0 | 0 | 0.532 | 106
2017-07-27 | 6.79 | 284 | 156 | 90 | 4 | 0 | 0 | 0 | 0 | 0.557 | 96
2017-07-28 | 6.59 | 317 | 174 | 90 | 5 | 0 | 0 | 0 | 0 | 0.503 | 112
2017-07-31 | 6.37 | 211 | 116 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 66.2
2017-08-01 | 6.46 | 244 | 134 | 50 | 4 | 0 | 0 | 0 | 0 | 0.25 | 81
2017-08-02 | 6.43 | 53 | 29 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 4
2017-08-03 | 6.97 | 157 | 86 | 40 | 5 | 1 | 1 | 0 | 0 | 0.037 | 23.24
2017-08-04 | 6.09 | 150 | 83 | 40 | 8 | 4 | 4 | 0 | 0 | 0 | 10
2017-08-07 | 6.81 | 150 | 83 | 60 | 8 | <1 | <1 | 0 | 0 | 0 | 11.3
2017-08-08 | 6.79 | 151 | 83 | 50 | 7 | 1 | 1 | 0 | 0 | 0.033 | 10.48
2017-08-09 | 6.82 | 146 | 80 | 30 | 10 | 4 | 4 | 0 | 0 | 0.306 | 11
2017-08-10 | 6.94 | 146 | 80 | 30 | 5 | 7 | 7 | 0 | 0 | 0.757 | 11
2017-08-11 | 6.27 | 154 | 85 | 5 | 10 | 28 | 25 | 3 | 0.289 | 2.108 | 10
2017-08-14 | 6.68 | 146 | 80 | 50 | 8 | 3 | 3 | 0 | 0 | 0.024 | 11
2017-08-15 | 6.4 | 133 | 73 | 40 | 5 | 4 | 4 | 0 | 0 | 0.127 | 10
2017-08-16 | 6.27 | 117 | 64 | 30 | 10 | 8 | 8 | 0 | 0 | 0 | 9
2017-08-17 | 6.56 | 140 | 77 | 50 | 5 | 3 | 3 | 0 | 0 | 0 | 17
2017-08-18 | 6.43 | 158 | 87 | 40 | 5 | 3 | 3 | 0 | 0 | 0.702 | 27
2017-08-21 | 9.23 | 946 | 520 | 160 | 6
2017-08-22 | 9.21 | 974 | 536 | 200 | 5 | 3 | 3 | 0 | 0.039 | 2.253 | 419
2017-08-23 | 8.86 | 820 | 451 | 90 | 5 | 5 | 5 | 0 | 0.024 | 2.117 | 314
2017-08-24 | 6.79 | 169 | 93 | 50 | 2 | 1 | 1 | 0 | 0 | 0.123 | 47
2017-08-25 | 6.78 | 173 | 95 | 30 | 2 | 19 | 10 | 9 | 0 | 0.111 | 52
2017-08-28 | 6.32 | 144 | 79 | 40 | 5 | 5 | 1 | 4 | 0 | 0.212 | 43
2017-08-29 | 6.21 | 140 | 77 | 30 | 4 | 0 | 0 | 0 | 0 | 0.212 | 42
2017-08-30 | 8.74 | 816 | 449 | 110 | 5
2017-08-31 | 7.79 | 558 | 307 | 70 | 5 | 11 | 6 | 5 | 0 | 1.228 | 252
2017-09-01 | 6.89 | 428 | 235 | 60 | 5 | 8 | 8 | 0 | 0 | 0.823 | 191
2017-09-04 | 7.3 | 404 | 222 | 50 | 2 |  |  |  | <0.01 | 1.03 | 202.81
2017-09-05 | 6.24 | 260 | 143 | 30 | 4 | 0 | 0 | 0 | 0 | 0.41 | 94
2017-09-06 | 6.31 | 272 | 150 | 70 | 5 | 0 | 0 | 0 | 0.15 | 0.415 | 114
2017-09-07 06:00 | 6.25 | 185 | 102 | 40 | 5 | 9 | 3.5 | 5.74 | 0.12 | 0.94 | 65.025
2017-09-08 06:00 | 6.22 | 199 | 109 | 40 | 4 | 9 | 3.68 | 5.21 | 0.11 | 0.67 | 79.662
2017-09-11 | 8.73 | 186 | 102 | 30 | 4 | 14 | 6 | 8 | 0.052 | 0 | 65.3
2017-09-12 06:00 | 8.52 | 139 | 76 | 20 | 4 | 21 | 10 | 11 | 0.18 | 0.03 | 39.372
2017-09-13 06:00 | 8.7 | 164 | 90 | 30 | 5 | 8 | 3.25 | 4.48 | 0.139 | 0.78 | 58.446
2017-09-14 06:00 | 8.79 | 227 | 125 | 30 | 4 | 9 | 3.97 | 5.31 | 0.167 | 0.471 | 71.927
2017-09-15 06:00 | 8.88 | 276 | 152 | 30 | 4 | 14 | 4.73 | 9.15 | 0.206 | 0.631 | 94.316
2017-09-18 06:00 | 8.96 | 607 | 334 | 80 | 4 | 34 | 0 | 34.18 | 0.176 | 0.843 | 276.25
2017-09-19 06:00 | 9.09 | 491 | 270 | 70 | 5 | 0 | 0 | 0 | <0.01 | <0.01 | 174.59
2017-09-20 06:00 | 8.97 | 483 | 266 | 60 | 4 | 76 | 20.36 | 55.92 | 1.096 | <0.01 | 443.87
2017-09-21 06:00 | 8.98 | 413 | 227 | 50 | 6
2017-09-22 06:00 | 9.17 | 410 | 226 | 40 | 4 | 10 | 6.79 | 2.97 | 0.127 | 0.883 | 256.02
2017-09-25 06:00 | 8.92 | 304 | 167 | 80 | 5 | 0 | <0.01 | <0.01 | <0.01 | 0.945 | 29
2017-09-29 06:00 | 8.96 | 310 | 171 | 50 | 4 | 1 | 0.64 | <0.01 | 0.153 | 0.791 | 120.955
2017-10-02 06:00 | 9.03 | 299 | 164 | 50 | 5 | 0 | <0.01 | <0.01 | 15.9107 | 1.2911
2017-10-03 06:00 | 9 | 293 | 161 | 60 | 4 | 0 | <0.01 | <0.01 | 0.131 | 0.449 | 118.065
2017-10-04 06:00 | 9.07 | 284 | 156 | 70 | 4 | 6 | 5.97 | <0.01 | 0.173 | 1.33 | 126.072
2017-10-05 06:00 | 9 | 309 | 170 | 60 | 4 | 2 | 1.82 | <0.01 | 0.235 | 0.798 | 125.902
2017-10-06 06:00 | 7.96 | 306 | 168 | 70 | 5 | 0 | <0.01 | <0.01 | 0.155 | 0.95 | 125.035
2017-10-09 06:00 | 6.96 | 221 | 122 | 40 | 4 | 0 | <0.01 | <0.01 | <0.01 | 0.505 | 84.677
2017-10-10 06:00 | 6.91 | 214 | 118 | 40 | 5 | 0 | <0.01 | <0.01 | 0.034 | 1.195 | 77.605
2017-10-11 06:00 | 7.3 | 216 | 119 | 50 | 4 | 2 | 1.65 | <0.01 | 0.221 | 0.448 | 80.682
2017-10-12 06:00 | 8.19 | 227 | 125 | 30 | 9 | 0 | <0.01 | <0.01 | 0.077 | 0.048 | 83.844
2017-10-13 06:00 | 6.78 | 327 | 180 | 60 | 6
2017-10-16 06:00 | 7 | 271 | 149 | 40 | 6 | 34 | 23.71 | 9.91 | 0.126 | 0.79 | 61.608
2017-10-17 06:00 | 7.14 | 270 | 149 | 40 | 4 | 38 | 24.98 | 13.21 | 0.169 | 1.248 | 51.765
2017-10-18 06:00 | 7.03 | 261 | 144 | 60 | 5 | 20 | 16.18 | 3.45 | <0.01 | 0.346 | 66.776
2017-10-19 06:00 | 7.2 | 280 | 154 | 75 | 5 | 36 | 24.38 | 11.82 | 0.125 | 0.893 | 63.597
2017-10-20 06:00 | 7.03 | 281 | 155 | 60 | 5 | 25 | 21.16 | 4.01 | <0.01 | 0.61 | 54.927
2017-10-23 06:00 | 7.19 | 287 | 158 | 60 | 4 | 22 | 22.02 | <0.01 | <0.01 | 0.646 | 51.748
2017-10-24 06:00 | 7.39 | 285 | 157 | 60 | 5 | 43 | 28.48 | 14.33 | 0.13 | 0.207 | 52.649
2017-10-25 06:00 | 7.45 | 291 | 160 | 60 | 4 | 31 | 23.27 | 7.29 | <0.01 |  | 51.442
2017-10-26 06:00 | 7.27 | 297 | 163 | 60 | 2
2017-10-27 06:00 | 7.11 | 323 | 178 | 60 | 2
2017-10-30 06:00 | 7.96 | 507 | 279 | 120 | 5 | 27 | 25.05 | 1.59 | <0.01 |  | 141.117
2017-10-31 06:00 | 7.63 | 499 | 274 | 105 | 4 | 23 | 22.11 | 1.09 | <0.01 | 1.364 | 144.466
2017-11-01 06:00 | 7.69 | 524 | 288 | 75 | 5 | 15 | 15.35 | <0.01 | <0.01 | 1.262 | 115.379
2017-11-02 06:00 | 7.53 | 515 | 283 | 135 | 5 | 38 | 31.53 | 6.14 | 0.032 | 0.595 | 164.9
2017-11-03 06:00 | 7.76 | 635 | 349 | 70 | 3 | 28 | 28.4 | <0.01 | <0.01 | 1.045 | 203.49
2017-11-06 06:00 | 6.78 | 663 | 365 | 150 | 29 | 225 | 130.6 | 94.1 | <0.01 | 0.051 | <0.01
2017-11-07 06:00 | 7.14 | 690 | 380 | 180 | 29 | 229 | 134.6 | 94.71 | <0.01 | <0.01 | 3.6567
2017-11-08 06:00 | 7.14 | 644 | 354 | 165 | 32 | 246 | 148.55 | 97.09 | 0.016 | 0.374 | 3.1977
2017-11-09 06:00 | 7.16 | 612 | 337 | 300 | 28 | 235 | 135.63 | 99.55 | <0.01 | <0.01 | <0.01
2017-11-10 06:00 | 7.28 | 649 | 357 | 315 | 32 | 224 | 130.48 | 93.48 | <0.01 | <0.01 | 0.3706
2017-11-13 06:00 | 8.34 | 1237 | 680 | 480 | 5 | 200 | 125 | 74.99 | <0.01 |  | 814.64
2017-11-14 06:00 | 9.21 | 2650 | 1458 | 720 | 10 | 122 | 113.98 | 8.32 | <0.01 | 5.962 | 917.83
2017-11-15 06:00 | 9.09 | 2350 | 1293 | 1050 | 6 | 172 | 124.65 | 47.07 | <0.01 |  | 946.05
2017-11-16 06:00 | 8.99 | 2220 | 1221 | 855 | 10 | 165 | 117.8 | 47.23 | <0.01 | <0.01 | 820.59
2017-11-17 06:00 | 8.97 | 2130 | 1172 | 570 | 6 | 177 | 123.18 | 53.34 | <0.01 | 4.523 | 750.72
2017-11-20 06:00 | 8.26 | 1430 | 787 | 460 | 11 | 335 | 196.03 | 138.83 | <0.01 |  | 250.58
2017-11-21 06:00 | 8.05 | 1163 | 640 | 380 | 56 | 186 | 183.68 | 2.07 | <0.01
2017-11-22 06:00 | 8.29 | 3360 | 1848 | 280 | 23 | 37 | 25.33 | 11.34 | 0.342 | 1.854 | 188.02
2017-11-23 06:00
2017-11-24 06:00 | 8.19 | 1113 | 612 | 310 | 43 | 313 | 183.55 | 129.85 | <0.01 | 0.923 | 187.68
2017-11-27 06:00 | 8.15 | 1134 | 624 | 260 | 43 | 317 | 185.98 | 131.32 | <0.01 | 5.304 | 175.27
2017-11-28 06:00 | 8.18 | 1101 | 606 | 340 | 43 | 319 | 191.55 | 127.06 | <0.01 | 0.741 | 158.015
2017-11-29 06:00 | 8.17 | 1135 | 624 | 320 | 42 | 305 | 178.68 | 126.61 | <0.01 | 0.583 | 172.21
2017-11-30 06:00 | 8.12 | 1126 | 619 | 400 | 42 | 284 | 168.2 | 116.24 | <0.01 | 0.606 | 212.466
2017-12-01 06:00 | 8.04 | 1143 | 629 | 290 | 34 | 287 | 167.38 | 119.64 | <0.01 | 0.752 | 189.516
2017-12-04 11:17 | 8.16 | 1107 | 609 | 360 | 44 | 330 | 192.15 | 137.72 | <0.01 | 0.815 | 162.588
2017-12-05 06:00 | 8.13 | 1112 | 612 | 560 | 42 | 305 | 178.55 | 126.44 | <0.01 | 0.559 | 154.462
2017-12-06 06:00 | 7.99 | 1079 | 593 | 370 | 42 | 336 | 205.4 | 131.08 | <0.01 |  | 149.192
2017-12-07 06:00 | 8.08 | 1128 | 620 | 320 | 47 | 349 | 203.43 | 145.67 | <0.01 | 0.284 | 166.787
2017-12-08 06:00 | 7.91 | 1071 | 589 | 290 | 40 | 333 | 193.4 | 139.56 | 0.034 | 1.236 | 151.538
2017-12-12 06:00 | 7.93 | 1042 | 573 | 320 | 42 | 341 | 199.63 | 141 | 0.016 |  | 116.025
2017-12-13 06:00 | 8.1 | 1060 | 583 | 290 | 47 |  |  | 136.33 | 0.031 |  | 120.343
2017-12-14 06:00 | 8.17 | 1062 | 584 | 300 | 43
2017-12-15 06:00 | 8.13 | 1036 | 570 | 280 | 47 | 322 | 184 | 138.21 | 0.156 |  | 109.123
2017-12-18 06:00 | 8.18 | 1043 | 574 | 240 | 39 | 301 | 176.25 | 124.93 | <0.01 |  | 81.583
2017-12-19 06:00 | 8.11 | 966 | 531 | 370 | 79
2017-12-20 06:00 | 8.15 | 1005 | 553 | 330 | 45 | 310 | 177.18 | 133.13 | 0.08 |  | 91.562
2017-12-21 06:00 | 8.14 | 1008 | 554 | 180 | 44 | 326 | 184.6 | 141.82 | 0.416 | 0.459 | 87.873
2017-12-22 06:00 | 7.86 | 999 | 549 | 230 | 44 | 292 | 168.43 | 123.66 | 0.207 |  | 68.578
2017-12-27 06:00 | 8.21 | 1024 | 563 | 300 | 41 | 353 | 203.1 | 149.45 | 0.439
2017-12-28 06:00 | 8.41 | 996 | 548 | 260 | 40 | 334 | 190.85 | 143.58 | 0.404
2017-12-29 06:00 | 8.44 | 1023 | 563 | 240 | 41
2018-01-02 06:00 | 8.38 | 1036 | 570 | 310 | 44 | 334 | 189.68 | 144.32 | 0.405
2018-01-03 06:00 | 8.54 | 1021 | 562 | 260 | 42 | 320 | 184.05 | 136.28 | 0.538 | 0.432
2018-01-04 09:17 | 8.43 | 1029 | 566 | 260 | 40 | 299 | 171.13 | 127.72 | 0.311 | 0.299 | 71.4
2018-01-05 06:00 | 8.34 | 1044 | 574 | 435 | 41 | 307 | 175.03 | 132.43 | 0.466 | 0.55 | 45.033
2018-01-08 06:00 | 8.27 | 996 | 548 | 320 | 42 | 333 | 192.85 | 139.93 | 0.065 | <0.01 | 72.437
2018-01-09 06:00 | 8.41 | 1028 | 565 | 330 | 41 | 283 | 163.85 | 119.15 | 0.533 |  | 61.608
2018-01-10 06:00 | 8.17 | 1024 | 563 | 350 | 42 | 291 | 168.95 | 121.77 | 0.345 |  | 60.673
2018-01-11 06:00 | 8.49 | 1042 | 573 | 440 | 42 | 296 | 170.9 | 124.76 | 0.122
2018-01-12 06:00 | 8.53 | 984 | 541 | 410 | 42 | 292 | 169.78 | 122.55 | 0.248 |  | 106.658
2018-01-15
2018-01-16 06:00 | 8.43 | 1017 | 559 | 210 | 43 | 285 | 165.35 | 120.13 | 0.146 |  | 63.92
2018-01-17 06:00 | 8.43 | 1049 | 577 | 215 | 44 | 320 | 179.2 | 140.55 | 0.307 | 0.786 | 92.327
2018-01-18 06:00 | 7.62 | 1694 | 932 | 275 | 10 | 281 | 164 | 117.18 | 0.418 |  | 133.705
2018-01-19 06:00 | 8.03 | 1020 | 561 | 180 | 36 | 224 | 131.43 | 92.62 | 0.082 |  | 148.529
2018-01-22 06:00 | 8.19 | 860 | 473 | 230 | 35 | 210 | 117.63 | 92.17 | 0.321 | 0.609 | 176.8
2018-01-23 06:00 | 8.32 | 866 | 476 | 330 | 33 | 198 | 113.53 | 84.91 | 0.053 | 0.516 | 144.602
2018-01-24 06:00 | 8.28 | 890 | 490 | 380 | 38 | 164 | 95.38 | 69.09 | <0.01 | 0.147 | 144.823
2018-01-25 09:25 | 8.05 | 932 | 513 | 380 | 37 | 209 | 119.08 | 89.75 | 0.156 | 1 | 165.393
2018-01-26 10:12 | 8.14 | 905 | 498 | 270 | 39 | 233 | 133.93 | 99.43 | 0.354 | 0.767
2018-01-29 06:00 | 7.9 | 927 | 510 | 340 | 36 | 197 | 114.48 | 82.08 | 0.123 | 0.949 | 110.942
2018-01-30 06:00 | 8.13 | 848 | 466 | 540 | 39 | 200 | 115.25 | 84.38 | 0.476 | 0.692 | 99.909
2018-01-31 06:00 | 8.25 | 933 | 513 | 400 | 36 | 207 | 121.4 | 85.12 | 0.256 | 0.537 | 127.279
2018-02-01 06:00 | 7.86 | 734 | 404 | 400 | 33 | 147 | 85.3 | 62.12 | 0.147 | 0.178 | 54.808
2018-02-02 06:00 | 8.19 | 850 | 468 | 330 | 36 | 163 | 97.5 | 65.23 | <0.01 | 0.215
2018-02-05 06:00 | 7.82 | 883 | 486 | 380 | 33 | 204 | 114.55 | 89.42 | 0.17 | 0.339 | 56.559
2018-02-06 06:00 | 8.54 | 879 | 483 | 320 | 32 | 152 | 94.68 | 56.99 | <0.01 |  | 38.386
2018-02-07 06:00 | 8.21 | 859 | 472 | 300 | 36 | 198 | 112.65 | 85.77 | 0.042 |  | 55.182
2018-02-08 06:00 | 8.07 | 847 | 466 | 420 | 34 | 198 | 111.08 | 86.55 | <0.01 |  | 60.282
2018-02-09 06:00 | 7.98 | 869 | 478 | 310 | 34 | 186 | 108.25 | 78.19 | <0.01 | 0.369 | 58.48
2018-02-12 06:00 | 7.55 | 964 | 530 | 360 | 36 | 183 | 103.6 | 79.05 | 0.019 | 0.328 | 59.415

## Closed Loop
Date | pH |  | TDS | M | Chloride | Total |  |  | Iron
Sample |  |  |  | Alkalinity |  | Hardness
TSL HOT LOOP
TSL Hot Loop | pH | Conductivity | TDS | Total | Chloride | Total | Calcium | Magnesium | Iron | Arsenic | Sodium | SO4 | MoO₄
|  | µs/cm |  | Alkalinity |  | Hardness | Hardness | Hardness
Date |  |  | mg/l | mg/l as CaCO3 | mg/l Cl- | mg/l as CaCO3 | mg/l as CaCO3 | mg/l as CaCO3 | mg/l Fe | mg/L | mg/L Na | mg/l | mg/l
OPERATION LIMITS
min | 9.5 | 100 | 50 | 100 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 200
max | 10.5 | 2000 | 1000 | 500 | 50 | 200 | 150 | 100 | 5 | 1 | 500 | 100 | 600
2017-01-04 | 8.98 | 1069 | 588 | 460 | 8 | 45 | 20 | 23 | 11.55 | 0.572 | 270.1 |  | 116.025
2017-01-05 | No Sample
2017-01-06 | No Sample
2017-01-09 | No Sample
2017-01-10 | No Sample |  |  | cor
2017-01-11 | 9.26 | 1382 | 760 | 685 | 6 | 66 | 31 | 35 | 19.59 | 0.827 | 337.4 |  | 117.1
2017-01-12 | No Sample
2017-01-13 | No Sample
2017-01-16 | No Sample
2017-01-17 | No Sample
2017-01-18 | No Sample
2017-01-19 | No Sample
2017-01-20 | 8.89 | 734 | 404 | 170 | 12 | 20 | 7 | 13 | 11.11 | 1.718 | 182.9 |  | 199
2017-01-23 | 8.81 | 792 | 436 | 200 | 7 | 28 | 10 | 18 | 10.95 | 1.571 | 182.9 | 57 | 204
2017-01-24 | No Sample
2017-01-25 | No Sample
2017-01-26 | 8.98 | 860 | 473 | 290 | 7 | 39 | 15 | 24 | 8.366 | 1.453 | 209.9 |  | 190
2017-01-27 | 9 | 884 | 486 | 260 | 5 | 47 | 19 | 28 | 8.022 | 1.289 | 210 | 77 | 188
2017-01-30 | 9.02 | 981 | 540 | 320 | 6 | 50 | 22 | 28 | 8.128 | 1.38 | 231.7 | 81 | 175
2017-01-31 | 9.08 | 981 | 540 | 290 | 8 | 44 | 21 | 23 | 7.684 | 1.44 | 229.7 |  | 171
2017-02-01 | No Sample
2017-02-02 | No Sample
2017-02-03 | No Sample
2017-02-06 | No Sample
2017-02-07 | No Sample
2017-02-08 | No Sample
2017-02-09 | No Sample
2017-02-10 | No Sample
2017-02-13 | No Sample
2017-02-14 | No Sample
2017-02-15 | No Sample
2017-02-16 | No Sample
2017-02-17 | No Sample
2017-02-20 | No Sample
2017-02-21 | No Sample
2017-02-22 | No Sample
2017-03-02 | No Sample
2017-03-03 | No Sample
2017-03-06 | No Sample
2017-03-08 | 8.79 | 951 | 523 | 250 | 4 | 34 | 15 | 19 | 9.582 | 1.277 | 216.5 |  | 200
2017-03-09 | 8.78 | 982 | 540 | 230 | 4 | 61 | 26 | 35 | 8.93 | 1.165 | 242.3 |  | 213
2017-03-13 | No Sample
2017-03-14 | No Sample
2017-03-15 | No Sample
2017-03-16 | No Sample
2017-03-20 | No Sample
2017-03-22 | No Sample
2017-03-23 | 8.63 | 980 | 539 | 380 | 5 | 16960 | 30 | 16930
2017-03-24 | 8.57 | 1006 | 553 | 520 | 9 | 290 | 70 | 220
2017-03-27 | No Sample
2017-03-28 | 8.42 | 1000 | 550 | 400 | 18 | 340 | 30 | 310
2017-03-29 | 8.41 | 1056 | 581 | 470 | 21 | 13850 | 50 | 13800
2017-03-30 | 8.41 | 1072 | 590 | 470 | 16 | 14850 | 40 | 14810
2017-03-31 | 8.36 | 1085 | 597 | 470 | 16 | 14450 | 30 | 14420 | 8.2 |  |  | 76
2017-04-01 | 8.89 | 339 | 186 | 270 | 6 | 100 | 80 | 20
2017-04-03 | 8.31 | 1169 | 643 | 500 | 18 | 60 | 32 | 28 |  |  |  | 73
2017-04-04 | No Sample
2017-04-05 | No Sample
2017-04-06 | No Sample
2017-04-07 | No Sample
2017-04-10 | 8.38 | 619 | 340 | 230 | 5 | 105 | 2 | 103 |  |  |  | 33
2017-04-11 | 8.35 | 656 | 361 | 260 | 6 | 240 | 30 | 210
2017-04-12 | 8.36 | 690 | 380 | 270 | 7 | 70 | 20 | 50
2017-04-13 | 8.34 | 763 | 420 | 300 | 8 | 150 | 20 | 130
2017-04-18 | No Sample
2017-04-19 | No Sample
2017-04-20 | 8.24 | 825 | 454 | 270 | 17 | 160 | 20 | 140
2017-04-21 | 8.17 | 847 | 466 | 370 | 18 |  | 20 |  |  |  |  | 44
2017-04-24 | No Sample
2017-04-25 | 7.86 | 952 | 524 | 300 | 18 |  | 0
2017-04-26 | No Sample
2017-04-27 | 7.7 | 991 | 545 | 490 | 18 |  | 0
2017-04-28 | No Sample
2017-05-02 | 7.18 | 1257 | 691 | 480 | 13 |  | 10
2017-05-03 | 7.09 | 1287 | 708 | 500 | 89 |  | 0
2017-05-05 | 7.49 | 1177 | 647 | 550 | 33 |  | 10 |  |  |  |  | 3
2017-05-08 | 6.82 | 579 | 318 | 290 | 5 |  | 10 |  |  |  |  | 17
2017-05-09 | 6.74 | 586 | 322 | 220 | 5 |  | 30
2017-05-10 | 6.82 | 415 | 228 | 200 | 8 |  | 30
2017-05-11 | 6.73 | 421 | 232 | 140 | 6 |  | 30
2017-05-12 | No Sample
2017-05-15 | No Sample
2017-05-16 | No Sample
2017-05-17 | No Sample
2017-05-18 | 7.32 | 1924 | 1058 | 780 | 11 |  | 20
2017-05-19 | 7.29 | 2090 | 1150 | 780 | 15 | 171 | 23 | 148 | 11.91 | 4.204 | 709.1 | 1250 | 398
2017-05-22 | 7.37 | 2170 | 1194 | 650 | 8 | 149 | 21 | 128 | 6.502 | 4.589 | 674.4 | 91 | 417
2017-05-23 | No Sample
2017-05-24 | No Sample
2017-05-26 | 7.78 | 2200 | 1210 | 660 | 8 | 132 | 21 | 111 | 5.421 | 4.283 | 625 | 89 | 464.3
2017-05-29 | 7.62 | 2190 | 1205 | 570 | 15 | 112 | 18 | 94 | 5.483 | 4.552 | 606.3 | 83 | 502
2017-05-30 | 7.54 | 2150 | 1183 | 600 | 7 | 112 | 16 | 96 | 5.281 | 4.611 | 635.1 |  | 533
2017-05-31 | 7.58 | 2210 | 1216 | 750 | 8 | 111 | 16 | 95 | 5.397 | 4.611 | 638.7 |  | 544
2017-06-01 | 8.11 | 2220 | 1221 | 500 | 8 | 119 | 23 | 96 | 5.352 | 4.885 | 627.7 |  | 506
2017-06-02 | 8.23 | 2080 | 1144 | 1000 | 11 | 110 | 12 | 98 | 4.832 | 3.931 | 624 | 80 | 520
2017-06-05 | 8.22 | 2090 | 11550 | 670 | 11 | 121 | 18 | 103 | 4.887 | 5.769 | 677.4 | 85 | 536
2017-06-06 | 9.37 | 2070 | 1139 | 1040 | 12 | 120 | 17 | 103 | 4.49 | 5.138 | 670.8 |  | 543
2017-06-07 | 8.3 | 2120 | 1166 | 750 | 8 | 119 | 18 | 101 | 4.211 | 4.732 | 713.1 |  | 531
2017-06-08 | No Sample
2017-06-09 | No Sample
2017-06-12 | No Sample
2017-06-13 | No Sample
2017-06-14 | No Sample
2017-06-15 | No Sample
2017-06-16 | No Sample
2017-06-19 | 8.58 | 2210 | 1216 | 690 | 8 | 110 | 18 | 92 | 4.947 | 4.788 | 680.2 | 53 | 600
2017-06-20 | 8.7 | 2230 | 1227 | 610 | 10 | 97 | 14 | 83 | 3.194 | 5.041 | 661.1 |  | 558
2017-06-21 | 8.68 | 2260 | 1243 | 1340 | 6 | 53 | 0 | 53 | 2.467 | 4.467 | 647.5 |  | 505
2017-06-22 | 8.57 | 2270 | 1249 | 1340 | 5 | 122 | 26 | 96 | 2.84 | 4.579 | 692 |  | 462
2017-06-23 | 7.88 | 2210 | 1216 | 590 | 5 | 134 | 12 | 122 | 3.509 | 6.086 | 733.4 | 110 | 335
2017-06-26 | 8.02 | 2400 | 1320 | 520 | 10 | 218 | 65 | 153 | 3.707 | 3.079 | 791.2 | 265 | 666
2017-06-27 | 8.15 | 2310 | 1271 | 1230 | 2 | 108 | 15 | 93 | 3.713 | 3.556 | 764.1 |  | 627
2017-06-28 | 8.27 | 2390 | 1315 | 880 | 11 | 111 | 18 | 93 | 3.298 | 3.853 | 726.1 |  | 491
2017-06-29 | 8.25 | 2390 | 1315 | 1180 | 11 | 108 | 16 | 92 | 3.321 | 4.689 | 769.8 |  | 493.3
2017-06-30 | 8.62 | 2590 | 1425 | 1110 | 28 | 123 | 19 | 104 | 3.868 | 7.073 | 849.9 | 135 | 562
2017-07-03 | 8.49 | 2430 | 1337 | 1260 | 30 | 119 | 14 | 105 | 3.672 | 6.632 | 895.9 | 120 | 549
2017-07-04 | 9.05 | 1816 | 999 | 1010 | 6 | 82 | 11 | 71 | 4.325 | 5.116 | 644 |  | 506
2017-07-05 | 8.93 | 1959 | 1077 | 990 | 7 | 76 | 8 | 68 | 3.567 | 3.959 | 683.2 |  | 473
2017-07-06 | No Sample
2017-07-07 | No Sample
2017-07-10 | No Sample
2017-07-11 | No Sample
2017-07-12 | No Sample
2017-07-13 | 9.56 | 2400 | 1320 | 790 | 19 | 119 | 25 | 94 | 6.237 | 4.108 | 787.3 |  | 480
2017-07-14 | No Sample
2017-07-17 | 9.6 | 2120 | 1166 | 1320 | 17 | 127 | 26 | 101 | 5.273 | 3.35 | 786.4 |  | 388
2017-07-18 | 8.75 | 2290 | 1260 | 1090 | 23 | 105 | 16 | 89 | 6.301 | 3.845 | 789.1 |  | 448
2017-07-19 | 8.78 | 2290 | 1260 | 880 | 67 | 112 | 18 | 94 | 4.927 | 4.409 | 831 |  | 399
2017-07-20 | 8.87 | 2550 | 1403 | 1260 | 72 | 117 | 20 | 97 | 4.559 | 3.545 | 829.4 |  | 406
2017-07-21 | 8.59 | 2540 | 1397 | 1090 | 30 | 114 | 19 | 95 | 3.832 | 3.794 | 833.2 |  | 397
2017-07-24 | 8.72 | 2480 | 1364 | 840 | 74 | 113 | 23 | 90 | 4.152 | 3.547 | 808.1
2017-07-25 | 8.6 | 2400 | 1320 | 870 | 35 | 100 | 21 | 79 | 3.167 | 8.303 | 725.1 |  | 336.4
2017-07-26 | 8.86 | 2190 | 1205 | 600 | 30 | 102 | 23 | 79 | 3.181 | 2.588 | 671.5 |  | 300
2017-07-27 | 8.76 | 2070 | 1139 | 850 | 30 | 88 | 16 | 72 | 6.268 | 3.327 | 664.3 |  | 314
2017-07-28 | 8.65 | 1883 | 1036 | 700 | 18 | 57 | 17 | 40 | 2.796 | 2.865 | 556 | 110 | 320
2017-07-31 | 10.27 | 1475 | 811 | 600 | 11 | 62 | 14 | 48 | 2.917 | 1.579 | 424.2 | 32 | 241.4
2017-08-01 | 10.3 | 1406 | 773 | 510 | 7 | 46 | 6 | 40 | 3.49 | 1.491 | 397 |  | 224
2017-08-02 | No Sample
2017-08-03 | No Sample
2017-08-04 | No Sample
2017-08-07 | No Sample
2017-08-08 | No Sample
2017-08-09 | No Sample
2017-08-10 | 9.48 | 730 | 402 | 230 | 7 | 44 | 14 | 30 | 8.883 | 2.272 | 182 |  | 77
2017-08-14 | 10.2 | 634 | 349 | 230 | 6 | 22 | 7 | 15 | 5.638 | 1.278 | 143.1 | 45 | 36
2017-08-15 | 8.7 | 682 | 375 | 220 | 7 | 32 | 11 | 21 | 6.93 | 1.33 | 170 |  | 35
2017-08-16 | 9 | 635 | 349 | 210 | 5 | 43 | 16 | 27 | 4.615 | 2.902 | 175.5 |  | 37
2017-08-17 | No Sample
2017-08-18 | No Sample
2017-08-21 | No Sample
2017-08-22 | 9.27 | 996 | 548 | 340 | 6 | 62 | 23 | 39 | 4.385 | 2.759 | 315.4 |  | 183
2017-08-23 | No Sample
2017-08-24 | 9.03 | 786 | 432 | 200 | 4 | 14 | 8 | 6 | 3.778 | 3.181 | 172.2 |  | 226.4
2017-08-25 | 9.23 | 749 | 412 | 230 | 4 | 33 | 14 | 19 | 4.058 | 2.382 | 201.8 | 20 | 228
2017-08-28 | 9.2 | 678 | 373 | 320 | 5 | 35 | 14 | 21 | 2.93 | 1.559 | 174.3 | 16 | 160
2017-08-29 | 8.88 | 698 | 384 | 140 | 5 | 24 | 10 | 14 | 2.473 | 1.605 | 175.3 |  | 141
2017-08-30 | 8.44 | 705 | 388 | 220 | 6
2017-08-31 | No Sample
2017-09-01 | No Sample
2017-09-04 | No Sample
2017-09-05 | No Sample
2017-09-06 | 7.81 | 859 | 472 | 270 | 5 | 75 | 26 | 49 | 6.984 | 5.385 | 207.8 |  | 222
2017-09-07 | No Sample
2017-09-08 06:00 | 8.23 | 1093 | 601 | 170 | 7 | 50 | 14.4 | 35.38 | 4.85 | 1.84 | 261.1 | 18 | 407.32
2017-09-11 | 9.67 | 1131 | 622 | 180 | 7 | 60 | 20 | 40 | 6.878 | 1.72 | 284.4 | 53 | 382.2
2017-09-12 06:00 | 9.61 | 1168 | 642 | 200 | 5 | 68 | 25 | 43 | 8.09 | 1.2 | 270.3 |  | 334.56
2017-09-13 06:00 | 9.68 | 1078 | 593 | 110 | 7 | 53 | 16.47 | 36.57 | 8.776 | 1.66 | 273.6 |  | 316.37
2017-09-14 | No Sample
2017-09-15 | No Sample
2017-09-18 | No Sample
2017-09-19 | No Sample
2017-09-22 06:00 | 9.85 | 1058 | 582 | 300 | 61 | 41 | 18.45 | 22.96 | 12.46 | 2.004 | 281.5 | 80 | 385.9
2017-09-25 06:00 | 9.92 | 1140 | 627 | 440 | 6 | 23 | 15.49 | 7.84 | 13.86 | 2.157 | 334.2 | 100 | 22
2017-09-26 06:00 | 9.83 | 1179 | 648 | 330 | 187 | 48 | 26.85 | 20.71 | 16.5 | 1.443 | 350
2017-09-28 06:00 | No Sample
2017-09-29 06:00 | 9.75 | 1383 | 761 | 400 | 25 | 47 | 25.5 | 21.67 | 25.74 | 2.388 | 456.6 | 224
2017-09-30
2017-10-01
2017-10-02 06:00
2017-10-03 06:00
2017-10-04 06:00
2017-10-05 06:00 | 9.99 | 1585 | 872 | 480 | 28 | 50 | 27.23 | 23.15 | 28.59 | 2.812 | 531.7 |  | 198.56
2017-10-06 06:00 | 9.06 | 1606 | 883 | 680 | 226 | 47 | 25.5 | 21.19 | 31.65 | 2.4 | 554.1 | 145 | 197.71
2017-10-09 06:00 | 8.91 | 1633 | 898 | 510 | 104 | 45 | 25.13 | 20.28 | 32.7 | 2.041 | 617.5 | 125 | 195.5
2017-10-10 06:00 | 8.49 | 1814 | 998 | 560 | 187 | 71 | 30.38 | 41.04 | 36.24 | 2.208 | 613.7 |  | 190.4
2017-10-11 06:00 | 8.64 | 1760 | 968 | 590 | 59 | 88 | 36.38 | 51.13 | 41.98 | 1.888 | 760.6 |  | 181.73
2017-10-12 06:00 | 8.75 | 1780 | 979 | 450 | 107 | 66 | 27.33 | 38.4 | 37.3 | 2.273 | 646.8 |  | 179.18
2017-10-13 06:00 | 8.78 | 1850 | 1018 | 480 | 128 | [6 empty] | 135
2017-10-16 06:00 | 8.88 | 1974 | 1086 | 410 | 123 | 70 | 32.15 | 38.27 | 44.48 | 1.573 | 730.9 | 236 | 206.72
2017-10-17 06:00 | 9.03 | 2070 | 1139 | 540 | 130 | 77 | 34.78 | 42.19 | 43.86 | 2.532 | 742.87 |  | 152.609
2017-10-18 06:00 | 9.09 | 2010 | 1106 | 600 | 150 | 61 | 27.83 | 33.55 | 43.56 | 1.79 | 760 |  | 192.61
2017-10-19
2017-10-20
2017-10-23
2017-10-24
2017-10-25
2017-10-26
2017-10-27
2017-10-30
2017-10-31
2017-11-01
2017-11-02 06:00 | 8.97 | 2780 | 1529 | 885 | 222 | 90 | 41.78 | 47.85 | 61 | 4.097 | 1177 |  | 276.08
2017-11-03
2017-11-06
2017-11-07
2017-11-08 06:00
2017-11-09 06:00 | 8.03 | 853 | 469 | 420 | 68 | 182 | 95.3 | 86.88 | 9.699 | <0.01 | 169.3 |  | 16.3591
2017-11-10 06:00 | 8.31 | 1127 | 620 | 600 | 59 | 169 | 94.23 | 74.58 | 9.119 | 0.568 | 214.7 | 171 | 94.69
2017-11-13 06:00 | 8.29 | 1282 | 705 | 630 | 17 | 131 | 80.78 | 50.64 | 13 |  | 320.5 | 290 | 111.367
2017-11-15 06:00 | 8.81 | 1681 | 925 | 615 | 16 | 129 | 90.78 | 38.57 | 16.48 |  | 474.4
2017-11-17 06:00 | 8.83 | 1875 | 1031 | 855 | 122 | 127 | 88.65 | 38.01 | 16.39 | <0.01 | 527.9 | 175 | 237.66
2017-11-20 06:00 | 9.24 | 1977 | 1087 | 650 | 129 | 142 | 91.33 | 50.59 | 20.17 |  | 564.6 | 325 | 248.71
2017-11-22 06:00 | 9.05 | 1895 | 1042 | 580 | 20 | 168 | 104.73 | 63.63 | 13.27 | 2.106 | 512.3 |  | 54.145
2017-11-23
2017-11-24
2017-11-25
2017-11-26
2017-11-27
2017-11-28
2017-11-29
2017-11-30
2017-12-01
2017-12-04 11:17 | 9.33 | 2470 | 1359 | 970 | 36 | 210 | 136.95 | 72.57 | 28.27 | 1.802 | 790.6 | 1150 | 334.9
2017-12-05 06:00 | 9.43 | 2500 | 1375 | 1180 | 126 | 205 | 133.53 | 71.01 | 30.16 | 1.579 | 801.2 |  | 275.91
2017-12-06 06:00 | 9.41 | 2540 | 1397 | 1130 | 128 | 167 | 106.68 | 60.48 | 26.6 |  | 812.1 |  | 360.57
2017-12-07 06:00 | 9.47 | 2540 | 1397 | 990 | 134 | 215 | 131.93 | 83.35 | 28.52 | 4.155 | 800.3 |  | 354.28
2017-12-08 06:00 | 9.39 | 2450 | 1348 | 940 | 91 | 222 | 136.15 | 86.14 | 28.58 | 5.53 | 759.3 | 340 | 333.37
2017-12-12 06:00 | 9.29 | 2380 | 1309 | 900 | 339 | 201 | 126.7 | 74.05 | 23.29 |  | 732.2 | 385 | 272.68
2017-12-13 06:00 | 9.39 | 2370 | 1304 | 1120 | 368 |  |  | 78.39 | 23.1 |  | 824.2 |  | 258.06
2017-12-14 06:00 | 9.43 | 2480 | 1364 | 780 | 345
2017-12-15 06:00 | 9.24 | 2540 | 1397 | 690 | 446 | 239 | 144.4 | 94.63 | 28.66 |  | 810.3 | 355
2017-12-19 06:00 | 9.21 | 2650 | 1458 | 1015 | 444
2017-12-20 11:39 | 9.41 | 2810 | 1546 | 1060 | 281 | 264 | 146.25 | 117.26 | 32.87 |  | 919.6
2017-12-21
2017-12-22
2017-12-28 06:00 | 8.12 | 3430 | 1887 | 920 | 34 | 334 | 161.85 | 171.83 | 37.87 |  | 1193
2017-12-29 06:00 | 8.16 | 3530 | 1942 | 610 | 37
2018-01-02 06:00 | 7.98 | 4610 | 2536 | 1110 | 37 | 331 | 159.2 | 172.28 | 35.63 |  | 1734
2018-01-05 06:00 | 8.15 | 4030 | 2217 | 1875 | 244 | 363 | 178 | 184.5 | 28.38 | 3.822 | 1340 | 1650 | 476.68
2018-01-08 06:00 | 8.19 | 3950 | 2173 | 1460 | 315 | 320 | 181.2 | 139.28 | 21.86 | 1.413 | 1400 | 515 | 485.86
2018-01-09 06:00 | 8.04 | 4130 | 2272 | 780 | 303 | 260 | 145.7 | 114.19 | 30.92 |  | 1344 |  | 328.27
2018-01-10
2018-01-11
2018-01-12
2018-01-15
2018-01-16
2018-01-17
2018-01-18 06:00 | 7.4 | 4370 | 2404 | 1170 | 5 | 363 | 161.38 | 201.47 | 43.09 |  | 1548 |  | 300.05
2018-01-19 06:00
2018-01-22 06:00
2018-01-23 06:00
2018-01-29 06:00 | 7.73 | 4170 | 2294 | 2840 | 7 | 410 | 178.08 | 231.49 | 62.24 | 4.814 | 1715 | 350 | 416.67
2018-01-30 06:00 | 7.59 | 4080 | 2244 | 2750 | 12 | 409 | 178.25 | 231.04 | 70.45 | 3.115 | 1699 |  | 384.03
2018-01-31 06:00 | 7.61 | 4150 | 2283 | 1950 | 5 | 435 | 192.93 | 241.98 | 72.95 | 2.964 | 1963 |  | 393.21
2018-02-01 06:00 | 7.49 | 4060 | 2233 | 2640 | 6 | [7 empty] | 1.6031
2018-02-02 06:00 | 7.73 | 4230 | 2327 | 2340 | 5 | 374 | 168.5 | 205.49 | 71.04 | 3.677 | 1851 | 600
2018-02-05 06:00 | 7.39 | 5330 | 2932 | 2920 | 6 | 445 | 209.83 | 235.38 | 86.4 | 6.219 | 1991 | 565 | 551.65
2018-02-06 06:00 | 7.56 | 5350 | 2943 | 2620 | 6 | 382 | 178.73 | 202.95 | 85.78 |  | 1885 |  | 605.03
2018-02-08 06:00 | 7.39 | 4780 | 2629 | 2440 | 6 | 422 | 182.45 | 239.32 | 86.56 |  | 1888 |  | 624.07
2018-02-09 06:00 | 7.23 | 4760 | 2618 | 2400 | 8 | 419 | 182.85 | 235.91 | 84.43 | 4.016 | 1933 | 495 | 604.86
2018-02-12 06:00 | 7.18 | 5290 | 2910 | 2480 | 8 | 395 | 172.08 | 223 | 76.92 | 3.992 | 1919 | 520 | 121.669