## full pipe
Full pipe capacity estimator
[5 empty] | Transitional |  | Rough | Smooth
[5 empty] | C-W | HW | M | Bla |  |  | Darcy
D | Sf | k | C | n | V | V | V | V | Re | La(lambda) | Sf | Re* | Flow Type | Q final
m | m/m | mm |  |  | m/sec | m/sec | m/sec | m/sec |  | m/m | m/m |  |  | cumecs
0.45 | 0.005 | 0.2 | 125 | 0.013 | 1.6065 | 1.535 | 1.268 | 2.0534 | 580205.3487 | 0.016966 | 0.0020396 | 11.8754 | transitional turb | 0.24401
A |  |  |  |  | Q | Q | Q | Q
sq.m |  |  |  |  | cumecs | cumecs | cumecs | cumecs
0.15896 |  |  |  |  | 0.25538 | 0.24401 | 0.20157 | 0.32642
D: Based on the following formulas:; n: 1; C-W V: Manning equation for rough turbulent flow |  | V = (0.397/2)D^2/3S^1/2
n: 2; C-W V: The Blasius equation for smooth turbulent flow |  | V = 75D^5/7Sf^4/7
n: 3; C-W V: Hazen - Williams equation for transitional turbulent flow |  | V = 0.355CD^0.63Sf^0.54
n: 4; C-W V: The Colebrook-White equation for transitional turbulent flow |  | V = -2(2gDSf)^1/2LOG(k/3.7D+2.5v/D(2gDSf)^1/2)
n: 5; C-W V: Moody equation |  | La (lambda) = 0.0055[1+(20 000 k/D + 10^6/Re)^1/3}
n: 6; C-W V: Reynolds roughness number |  | Re* = Re(k/D)(La/8)^1/2
n: 7; C-W V: Darcy equation |  | hf = La*L*V^2/2gD
n: 8; C-W V: Reynold equation |  | Re = VD/v
n: 9; C-W V: Continuity equation |  | Q = VA
Notice: | Flow is smooth turbulent if Re* < 4. Blasius equation is used for discharge calculations.
Flow is transitional turbulent if 4 <= Re* < 60.
For discharge calculations at transitional turbulent flow - both Hazen - Williams and Colebrook - White equation can be used.
However the use of Hazen - Williams equation is not recommended when pipe velocity exceeds 3.0 m/sec.
Flow is of rough turbulent type when Re* > 60. Manning equation is used for discharge computations at this type of flow.
[5 empty] | Instructions: |  | 1 | Type pipe dia and grade in yellow cells
| Project: | North Head wetlands - subcatchment 1 |  |  |  |  | 2 | Type appropriate roughness factors in green cells
| Reference: |  | 1133 |  |  |  | 3 | Read flow type and final flow rate in cells N6 and O6
[7 empty] | 4 | Good luck

## partial pipe
|  | Partial filling of a pipe / headloss in the pipe flowing partially full | [11 empty] | Instructions:
D | ho | yo | alfa | F | F | P | R | R | n | So | Qgrav
m | m |  | rad | sq.m | sq.m | m |  |  |  | m/m | cumecs |  | A. General
2.4 | 0.025 | 0.010417 | 0.20448 | 0.0081232 | 0.0081394 | 0.49075 | 0.016588 | 0.016586 | 0.013 | 0.01 | 0.0040638
Q | ho grav | yo | L | V | hf | Fr | B | H | hc | t | 1 | Yellow cells are for input data
cumecs | m |  | m | m/sec | m |  | m | m | m | Pa | 2 | Grey cells are for output data
0.005 | 0.021989 | 0.0091621 | 45 | 0.6143 | 0.6785 | 2.1312 | 0.48734 | 0.041222 | 0.032101 | 1.627
If flow rate is known this spreadsheet can calculate normal
Formulas used: |  | t: flow depth for uniform gravity flow and headloss for a given
diameter and length of pipe.
[11 empty] | 1 | Type Q,D,n,So and L in yellow cells
[11 empty] | 2 | Read ho grav in cellB7
[11 empty] | 3 | Type the value of B7 as ho in cellB4
[11 empty] | 4 | Read hf in cell F7
If flow depth is known this spreadsheet can calculate
the flow rate for uniform gravity flow and headloss for a given
diameter and length of pipe.
[11 empty] | 1 | Type ho,D,n,So and L in yellow cells
[11 empty] | 2 | Read Q grav in cell L4
[11 empty] | 3 | Type the value of L4 as Q in cell A7
[11 empty] | 4 | Read hf in cell F7
If both flow depth and flow rate are known this spreadsheet
can calculate headlosses in the pipe.
[11 empty] | 1 | Type Q,ho,D,n,So and L in yellow cells
[11 empty] | 2 | Read hf in cell F7

## circular pipe
| Circular culvert / Throttling pipe flow estimator | [5 empty] | Based on chapters 9.1 - 9.33 , Willi H Hager "Wastewater Hydraulics" Springer 1999
D | Ho | Hu | So | n | L | Rough.# | Yo | Flow type |  |  | Project No | Western corts
m |  | m | m/m |  | m | full pipe |  |  |  |  | Date | 2010-03-04
0.2 | 1 | 0.2 | 0.005 | 0.013 | 1 | 1.3281 | 5 | pressurised
N/A
R*d | Rd | jd | Hd | h/l culvert | qd | Q
|  |  | m | m |  | cub.m/sec | free | transitional flow type
0.071738 | 0.014175 | 0.025 | 0.805 | 0.17988 | N/A | 0.11488 | 1.3168 | N/A |  |  | Operational Diagram
Qc max | Qcr | Q uni | Qgate tr | Qpress tr | Qpress | Qgate | Quni |  | Ho |  |  | Hu
free
N/A | 0.3508 | 0.16873 | 0.083064 | 0.099506 | 0.11488 | 0.083122 | 0.023839
f | Yt | Cd | Q simple culvert | Qor | Sf | Fd | Qunifull
0.19 | -324 | 0.64 | N/A | 0.079824 | 0.8 | N/A | 0.023839
[10 empty] | So | D
Logic:
Ho and Hu are Energy Heads u/s and d/s of culvert respectively. |  |  |  |  | So and Sf are Energy and pipe's gradients respectively. D is a pipe diameter.
| is pipe roughness characteristic (5.31). |  |  | L is culvert's length. Yo =Ho/D and Fd is pipe Froude number
Free Flow | in the culvert can be either critical, uniform or gated. Flow is critical whenever | [5 empty] | >2. | Maximum filling ratio should be 95%. Yo is generally lower than 1.20.
If Sf exceeds So hydraulic jump may develop in the pipe leading to the formation of standing waves and if filling ratio is larger than 90% to choking of the pipe(usually near the
outlet).
For larger approach level 1.2<Yo<1.5 and free culvert flow, gated flow appears when the u/s section is submerged sealing the culvert's inlet against airflow.
Pressurised flow develops when outlet of the culvert is submerged (choked) and Yo is equal or larger than 1.0.
Transition between gated and pressurised flow is analysed using roughness characteristics Rd and Rd* as per chapter 9.33 as well as possibilities of outlet choking due to
hydraulic jump formation and/or high filling ratio. Then the choice is made between gated and pressurised flow for a transitional flow type (this selection is automatic).
It is a well known fact that for the culvert flow situation a free surface flow often needs more head than pressurised flow. Also supercritical flow in the pipe is unstable leading
to formation of waves,h/jumps etc thus discharge under these conditions (described as "critical" in the program) may be lower than that under the "uniform" flow conditions.
Please note that the sharp-crested inlet configuration (Cd=0.64) is considered for transitional gated flow. For Qgate coefficient Cd can be changed in cell C15.
The approach taken in this spreadsheet is based on formulas valid for a long culvert (L/D>=10).
This spreadsheet is set up to automatically compute the discharge through the pipe/culvert for the flow situation described by the input parameters(Ho;Hu;n;So;D;L;Cd).
The final flow rate appears in cell G9 (brown font).
Flowrates for each flow situation are displayed in cells A13-H13 and D15,E15 and H15. It allows the user to compare the floweret selected by the program to other relevant
Flowrates and make his/her own judgements. |  |  |  | The Flowrates calculated by this spreadsheet are on the conservative side.
To use this program please follow these easy steps: |  |  |  |  | 1 | Type input data in yellow cells
[5 empty] | 2 | Read flow type in cells I5 and I9
[5 empty] | 3 | Read culvert discharge in cell G9 |  |  | Good luck
Abbreviations and formulas used in the spreadsheet
Qcmax | Maximum free flow discharge for this situation (9.6)
Qcr | Discharge for "critical" flow situation |  |  |  | > 2
Quni | Discharge for "uniform" flow situation |  |  |  |  | 5. Other formulas used
Qgate tr. | Discharge for transitional-gated flow situation
Q press. tr | Discharge for transitional-pressurised flow situation
Q press. tr | Discharge for "pressurised" flow situation
Qgate | Discharge for "gated" flow situation
Q uni free | Free uniform discharge
Q uni full | Uniform discharge for the 95% full pipe
Q simple culvert |  | Discharge calculated using formulas for a "simple culvert" (9.9 - 9.13)
Qor | Discharge calculated using small orifice formulae with Cor = 0.64
1. Free flow
Uniform flow
Critical flow
4. Transitional flow
2. Gate flow
3. Pressurised flow
.